Verification test data for Test #6:

Specimen overview:

6

14” X 14” X 2” PL

Geometric Parameters

Cantilever Height – 92.5” = 2349.5mm

Column size – W8X48

Section Depth = 8.5” = 215.9mm

Flange Width = 8.11” = 206mm

Plate size = 355.6mm square X 50.8mm thick

Anchor rod holes = 33.34mm diameter, centered at a point 38mm from each edge of the plate

Anchor rod diameter = 0.75 inch unthreaded, 0.65 inch threaded. The threaded portion extends from the top of the rod to 2 inches below the concrete surface.

Grout Pad Thickness = 2 inches

Material Parameters (measured)

Anchor Rods (Nominally ASTM 1554 Grade 105, i.e., 105ksi)

Yield Stress – 114ksi = 786 MPa

Ultimate Stress – 146ksi = 1010 MPa

Base Plate (Nominally ASTM A36)

Yield Stress – 38.4ksi = 264.6MPa

Ultimate Stress – 72.1ksi = 496.8MPa

Column (Nominally A992 Grade 50)

Concrete Compressive Strength (on day of testing) = 4.34ksi = 29.9MPa

Grout Compressive Strength (on day of testing) = 9.4ksi = 64.76MPa

Testing Parameters

Axial force = 92.45kips = 411kN

Cyclic lateral loading as per SAC Loading Protocol (details upon request).

Attached is an Excel file, designed for model validation.

- The test is cyclic and produces a hysteretic curve. The monotonic envelope is determined by considering the maximum base moment for any given lateral displacement. The anchor forces corresponding to these peak moments are also recovered for validation

- The anchor forces are not directly measured, but rather inferred from the anchor strains that are directly measured. This transformation is based on a measured stress-strain response of anchor rods tested separately.

- The attached Excel columns are self-explanatory in terms of the quantities they plot.

- The envelopes are recovered from the positive quadrant, the negative quadrant is very similar.

- Forces from the anchor rods on the tension side are plotted. Anchor rod forces on the compression side go to approximately zero since the bearing stress take most of the compression.

Mode of Failure

Spalling of grout and anchor rod yielding. No fracture.  No plate yielding.